SERVICE MANUAL

AIR CONDITIONER

SUPER DC INVERTER MULTI FREE MATCH

LOOP SERIES

U2MRSL(2)-14

U2MRSL(2)-18

U2MRSL(3)-21

U2MRSL(3)-27

U2MRSL(4)-28

U2MRSL(4)-36

U2MRSL(5)-36

DC MULTI OUTDOOR UNITS

CONTENTS

1. General information of Outdoor Units	2

2. Features	3

3. Dimensions	4

4. Wiring Diagram	7

5. Refrigeration Cycle Diagram	10

6. Indoor units combination	12

7. Installation Details	15

8. Electronic control function	25

9. Troubleshooting	31

# General information of Outdoor Units

| Model name | Dimension (mm) | Compressor |
| --- | --- | --- |
| U2MRSL(2)-14 | 845x320x700 | DA130M1C-31FZ |
| U2MRSL(2)-18 | 845x320x700 | DA150S1C-20FZ |
| U2MRSL(3)-21 | 845x320x700 | DA150S1C-20FZ |
| U2MRSL(3)-27 | 900x315x860 | DA250S2C-30MT |
| U2MRSL(4)-28 | 900x315x860 | DA250S2C-30MT |
| U2MRSL(4)-36 | 990x345x965 | TNB306FPGMC-L |
| U2MRSL(5)-36 | 990x345x965 | TNB306FPGMC-L |

# Features

# Dimensions

U2MRSL(2)-14, U2MRSL(2)-18, U2MRSL(3)-21

U2MRSL(3)-27, U2MRSL(4)-28

U2MRSL(4)-36, U2MRSL(5)-36

# Wiring Diagram

U2MRSL(2)-14,U2MRSL(2)-18

U2MRSL(3)-27,U2MRSL(3)-21

U2MRSL(4)-28

U2MRSL(4)-36

U2MRSL(5)-36

# Refrigeration Cycle Diagram

  - Refrigeration circuit drawing of inverter 1 drive 2 type

4.2 Refrigeration circuit drawing of inverter 1 drive 3 type

4.3 Refrigeration circuit drawing of inverter 1 drive 4 type

4.4 Refrigeration circuit drawing of inverter 1 drive 5 type

# Indoor units combination

#### Indoor unit combination for U2MRSL(2)-14

| One unit | Two unit |
| --- | --- |
| 7 | 7+7 | 9+9 |
| 9 | 7+9 | 9+12 |
| 12 | 7+12 |  |
| 18 |  |  |

#### Indoor unit combination for U2MRSL(2)-18

| One unit | Two unit |
| --- | --- |
| 7 | 7+7 | 9+9 |
| 9 | 7+9 | 9+12 |
| 12 | 7+12 | 9+18 |
| 18 | 7+18 | 12+12 |

#### Indoor unit combination for U2MRSL(3)-21

| One unit | Two unit | Three unit |
| --- | --- | --- |
| 7 | 7+7 | 9+9 | 7+7+7 | 7+9+12 |
| 9 | 7+9 | 9+12 | 7+7+9 | 9+9+9 |
| 12 | 7+12 | 9+18 | 7+7+12 | 9+9+12 |
| 18 | 7+18 | 12+12 | 7+9+9 |  |

#### Indoor unit combination for U2MRSL(3)-27

| One unit | Two unit | Three unit |
| --- | --- | --- |
| 7 | 7+7 | 9+9 | 12+18 | 7+7+7 | 7+9+9 | 7+12+18 | 9+12+12 |
| 9 | 7+9 | 9+12 | 18+18 | 7+7+9 | 7+9+12 | 9+9+9 | 9+12+18 |
| 12 | 7+12 | 9+18 |  | 7+7+12 | 7+9+18 | 9+9+12 | 12+12+12 |
| 18 | 7+18 | 12+12 |  | 7+7+18 | 7+12+12 | 9+9+18 |  |

#### Indoor unit combination for U2MRSL(4)-28

| One unit | Two unit | Three unit | Four unit |
| --- | --- | --- | --- |
| 7 | 7+7 | 9+9 | 12+18 | 7+7+7 | 7+9+9 | 9+9+9 | 7+7+7+7 | 7+7+9+9 | 7+9+9+12 | 7+7+7+7 |
| 9 | 7+9 | 9+12 | 18+18 | 7+7+9 | 7+9+12 | 9+9+12 | 7+7+7+9 | 7+7+9+12 | 7+9+12+12 | 7+7+7+9 |
| 12 | 7+12 | 9+18 |  | 7+7+12 | 7+9+18 | 9+9+18 | 7+7+7+12 | 7+7+12+12 | 9+9+9+9 | 7+7+7+12 |
| 18 | 7+18 | 12+12 |  | 7+7+18 | 7+12+12 | 9+12+12 | 7+7+7+18 | 7+9+9+9 | 9+9+9+12 | 7+7+7+18 |
|  |  |  |  |  | 7+12+18 |  |  |  |  |  |

#### Indoor unit combination for U2MRSL(4)-36

| One unit | Two unit | Three unit | Four unit |
| --- | --- | --- | --- |
| 7 | 7+7 | 9+9 | 12+12 | 7+7+7 | 7+12+12 | 9+12+18 | 7+7+7+7 | 7+7+12+12 | 7+9+12+18 | 9+9+12+12 |
| 9 | 7+9 | 9+12 | 12+18 | 7+7+9 | 7+12+18 | 9+18+18 | 7+7+7+9 | 7+7+12+18 | 7+9+18+18 | 9+9+12+18 |
| 12 | 7+12 | 9+18 | 18+18 | 7+7+12 | 7+18+18 | 12+12+12 | 7+7+7+12 | 7+7+18+18 | 7+12+12+12 | 9+12+12+12 |
| 18 | 7+18 |  |  | 7+7+18 | 9+9+9 | 12+12+18 | 7+7+7+18 | 7+9+9+9 | 7+12+12+18 | 9+12+12+18 |
|  |  |  |  | 7+9+9 | 9+9+12 | 12+18+18 | 7+7+9+9 | 7+9+9+12 | 9+9+9+9 | 12+12+12+12 |
|  |  |  |  | 7+9+12 | 9+9+18 |  | 7+7+9+12 | 7+9+9+18 | 9+9+9+12 | 12+12+12+18 |
|  |  |  |  | 7+9+18 | 9+12+12 |  | 7+7+9+18 | 7+9+12+12 | 9+9+9+18 |  |

#### Indoor unit combination for U2MRSL(5)-36

| One Unit | Two Unit | Three Unit |
| --- | --- | --- |
| 7 | 7+7 | 9+12 | 7+7+7 | 7+9+18 | 9+9+18 | 12+18+18 |
| 9 | 7+9 | 9+18 | 7+7+9 | 7+12+12 | 9+12+12 | 18+18+18 |
| 12 | 7+12 | 12+12 | 7+7+12 | 7+12+18 | 9+12+18 |  |
| 18 | 7+18 | 12+18 | 7+7+18 | 7+18+18 | 9+18+18 |  |
|  | 9+9 | 18+18 | 7+9+9 | 9+9+9 | 12+12+12 |  |
|  |  |  | 7+9+12 | 9+9+12 | 12+12+18 |  |
| Four Unit |
| 7+7+7+7 | 7+7+9+18 | 7+9+9+18 | 7+12+18+18 | 9+9+18+18 |
| 7+7+7+9 | 7+7+12+12 | 7+9+12+12 | 9+9+9+9 | 9+12+12+12 |
| 7+7+7+12 | 7+7+12+18 | 7+9+12+18 | 9+9+9+12 | 9+12+12+18 |
| 7+7+7+18 | 7+7+18+18 | 7+9+18+18 | 9+9+9+18 | 12+12+12+12 |
| 7+7+9+9 | 7+9+9+9 | 7+12+12+12 | 9+9+12+12 | 12+12+12+18 |
| 7+7+9+12 | 7+9+9+12 | 7+12+12+18 | 9+9+12+18 |  |
| Five Unit |
| 7+7+7+7+7 | 7+7+7+9+18 | 7+7+9+12+18 | 7+9+9+12+18 | 9+9+9+12+12 |
| 7+7+7+7+9 | 7+7+7+12+18 | 7+7+12+12+18 | 7+9+12+12+12 | 9+9+9+12+18 |
| 7+7+7+7+12 | 7+7+7+18+18 | 7+9+9+9+9 | 7+9+12+12+18 | 9+9+12+12+12 |
| 7+7+7+7+18 | 7+7+9+9+9 | 7+9+9+9+12 | 9+9+9+9+9 | 9+12+12+12+12 |
| 7+7+7+9+9 | 7+7+9+9+12 | 7+9+9+9+18 | 9+9+9+9+12 | 12+12+12+12+12 |
| 7+7+7+9+12 | 7+7+9+9+18 | 7+9+9+12+12 | 9+9+9+9+18 |  |

# Installation Details

## 7.1 Wrench torque sheet for installation

| Outside diameter | Torque | Additional tightening torque |
| --- | --- | --- |
| mm | N.cm | N.cm |
| Ф6.35 | 1500(153kgf.cm) | 1600(163kgf.cm) |
| Ф9.52 | 2500(255kgf.cm) | 2600(265kgf.cm) |
| Ф12.7 | 3500(357kgf.cm) | 3600(367kgf.cm) |

## 7.2 Connecting the cables

The power cord of connect should be selected according to the following specifications sheet.

| Rated current of appliance | Nominal cross-sectional area (mm²) |
| --- | --- |
| >3 and ≤6 | 0.75 |
| >6 and ≤10 | 1 |
| >10 and ≤16 | 1.5 |
| >16 and ≤25 | 2.5 |

The cable size and the current of the fuse or switch are determined by the maximum current indicated on the nameplate which located on the side panel of the unit. Please refer to the nameplate before selecting the cable, fuse and switch.

## 7.3 Pipe length and the elevation

Maximum piping length and height difference

|  | 1 drive 2 | 1 drive 3 | 1 drive 4 | 1 drive 5 |
| --- | --- | --- | --- | --- |
| Max. length for all rooms (m) | 30 | 45 | 60 | 75 |
| Max. length for one IU (m) | 20 | 25 | 30 | 30 |
| Max. height difference between IU and OU (m) | OU higher than IU | 10 | 10 | 10 | 10 |
|  | OU lower than IU | 15 | 15 | 15 | 15 |
| Max. height difference between IUs (m) | 10 | 10 | 10 | 10 |

Additional refrigerant charge

|  | 1 drive 2 | 1 drive 3 | 1 drive 4 | 1 drive 5 |
| --- | --- | --- | --- | --- |
| Chargeless pipe length (m) | 10 | 15 | 20 | 25 |
| Additional refrigerant charge (g) | 15 x (length for all rooms - 10) | 15 x (length for all rooms - 15) | 15 x (length for all rooms - 20) | 15 x (length for all rooms - 25) |

Caution:

- Refrigerant pipe diameter is different according to indoor unit to be connected. When using the extension pipe, refer to the tables below.

- When refrigerant pipe diameter is different from that of outdoor unit union (for 18K indoor unit), additional transfer connector needs to be used on outdoor unit union.

| Indoor unit | Extension pipe diameter (mm/inch) |
| --- | --- |
| Model | Pipe diameter (mm/inch) |  |
| 7K,9K,12K | Liquid | 6.35(1/4) | Liquid | 6.35(1/4) |
|  | Gas | 9.52(3/8) | Gas | 9.52(3/8) |
| 18K | Liquid | 6.35(1/4) | Liquid | 6.35(1/4) |
|  | Gas | 12.7(1/2) | Gas | 12.7(1/2) |
| Outdoor unit union diameter (mm/inch) |
| Indoor unit A/B/C/D | Liquid | 6.35(1/4) |
|  | Gas | 9.52(3/8) |

## 7.4 Installation for the first time

Air and moisture in the refrigerant system have undesirable effects as below:

- Pressure in the system rises.

- Operating current rises.

- Cooling or heating efficiency drops.

- Moisture in the refrigerant circuit may freeze and block capillary tubing.

- Water may lead to corrosion of parts in the refrigerant system.

Therefore, the indoor units and the pipes between indoor and outdoor units must be leak tested and evacuated to remove gas and moisture from the system.

Gas leak check (Soap water method):

Apply soap water or a liquid neutral detergent on the indoor unit connections or outdoor unit connections by a soft brush to check for leakage of the connecting points of the piping. If bubbles come out, the pipes have leakage.

1. Air purging with vacuum pump

- Completely tighten the flare nuts of the indoor and outdoor units, confirm that both the 2-way and 3-way valves are set to the closed position.

- Connect the charge hose with the push pin of handle lo to the 3-way valves gas service port..

- Connect the charge hose of handle hi connection to the vacuum pump.

- Fully open the handle Lo of the manifold valve.

- Operate the vacuum pump to evacuate.

- Make evacuation for 30 minutes and check whether the compound meter indicates -0.1Mpa. If

the meter does not indicate -0.1Mpa after pumping 30 minutes, it should be pumped 20 minutes more. If the pressure can’t achieve -0.1Mpa after pumping 50 minutes, please check if there are some leakage points.

Fully close the handle Lo valve of the manifold valve and stop the operation of the vacuum pump. Confirm that the gauge needle does not move (approximately 5 minutes after turning off the vacuum pump).

- Turn the flare nut of the 3-way valves about 45° counterclockwise for 6 or 7seconds after the gas

coming out, then tighten the flare nut again. Make sure the pressure display in the pressure indicator is a little higher than the atmosphere pressure. Then remove the charge hose from the 3 way valve.

- Fully open the 2 way valve and 3 way valve and securely tighten the cap of the 3 way valve.

2. Air purging by refrigerant

Procedure:

1). Confirm that both the 2-way and 3-way valves are set to the closed position.

2). Connect the charge set and a charging cylinder to the service port of the 3-way valve.

3). Air purging.

Open the valves on the charging cylinder and the charge set. Purge the air by loosening the flare nut on the 2-way valve approximately 45’ for 3 seconds then closing it for 1 minute; repeat 3 times.

After purging the air, use a torque wrench to tighten the flare nut on the 2-way valve.

4). Check the gas leakage.

Check the flare connections for gas leakage.

5). Discharge the refrigerant.

Close the valve on the charging cylinder and discharge the refrigerant by loosening the flare nut on the 2-way valve approximately 45’ until the gauge indicates 0.3 to 0.5 Mpa.

6). Disconnect the charge set and the charging cylinder, and set the 2-way and 3-way valves to the open position.

Be sure to use a hexagonal wrench to operate the valve stems.

7). Mount the valve stems nuts and the service port cap.

Be sure to use a torque wrench to tighten the service port cap to a torque 18N·m.

Be sure to check the gas leakage.

3. Adding the refrigerant if the pipe length >5m

Procedure:

1). Connect the charge hose to the charging cylinder, open the 2-way valve and the 3-way valve.

Connect the charge hose which you disconnected from the vacuum pump to the valve at the bottom of the cylinder. If the refrigerant is R410A, make the cylinder bottom up to ensure the liquid charge.

2). Purge the air from the charge hose.

Open the valve at the bottom of the cylinder and press the check valve on the charge set to purge the air (be careful of the liquid refrigerant).

3) Put the charging cylinder onto the electronic scale and record the weight.

4) Operate the air conditioner at the cooling mode.

5) Open the valves (Low side) on the charge set and charge the system with liquid refrigerant.

6).When the electronic scale displays the proper weight (refer to the table), disconnect the charge hose from the 3-way valve’s service port immediately and turn off the air conditioner before disconnecting the hose.

7). Mount the valve stem caps and the service port

Use torque wrench to tighten the service port cap to a torque of 18N.m.

Be sure to check for gas leakage.

## 7.5 Adding the refrigerant after running the system for many years

Procedure:

1). Connect the charge hose to the 3-way service port, open the 2-way valve and the 3-way valve.

Connect the charge hose to the valve at the bottom of the cylinder. If the refrigerant is R410A, make the cylinder bottom up to ensure liquid charge.

2). Purge the air from the charge hose.

Open the valve at the bottom of the cylinder and press the check valve on the charge set to purge the air (be careful of the liquid refrigerant).

3) Put the charging cylinder onto the electronic scale and record the weight.

4) Operate the air conditioner at the cooling mode.

5) Open the valves (Low side) on the charge set and charge the system with liquid refrigerant.

6).When the electronic scale displays the proper weight (refer to the gauge and the pressure of the low side), disconnect the charge hose from the 3-way valve’s service port immediately and turn off the air conditioner before disconnecting the hose.

7). Mount the valve stem caps and the service port

Use torque wrench to tighten the service port cap to a torque of 18N.m.

Be sure to check for gas leakage.

## 7.6 Re-installation while the indoor unit need to be repaired

1. Collecting the refrigerant into the outdoor unit

Procedure

1). Confirm that both the 2-way and 3-way valves are set to the opened position

Remove the valve stem caps and confirm that the valve stems are in the opened position.

Be sure to use a hexagonal wrench to operate the valve stems.

2). Connect the charge hose with the push pin of handle lo to the 3-way valves gas service port.

3). Air purging of the charge hose.

Open the handle Lo valve of the manifold valve slightly to purge air from the charge hose for 5 seconds and then close it quickly.

4). Set the 2-way valve to the close position.

5). Operate the air conditioner at the cooling cycle and stop it when the gauge indicates 0.1MPa.

6). Set the 3-way valve to the closed position immediately

Do this quickly so that the gauge ends up indicating 0.3 to 0.5Mpa.

Disconnect the charge set, and tighten the 2-way and 3-way valve’s stem nuts.

Use a torque wrench to tighten the 3-way valves service port cap to a torque of 1.8 kgf.m.

Be sure to check for gas leakage.

2. Air purging by the refrigerant

Procedure:

1). Confirm that both the 2-way and 3-way valves are set to the closed position.

2). Connect the charge set and a charging cylinder to the service port of the 3-way valve

Leave the valve on the charging cylinder closed.

3). Air purging.

Open the valves on the charging cylinder and the charge set. Purge the air by loosening the flare nut on the 2-way valve approximately 45’ for 3 seconds then closing it for 1 minute; repeat 3 times.

After purging the air, use a torque wrench to tighten the flare nut on the 2-way valve.

4). Check the gas leakage

Check the flare connections for gas leakage.

5). Discharge the refrigerant.

Close the valve on the charging cylinder and discharge the refrigerant by loosening the flare nut on the 2-way valve approximately 45’ until the gauge indicates 0.3 to 0.5 Mpa.

6). Disconnect the charge set and the charging cylinder, and set the 2-way and 3-way valves to the open position

Be sure to use a hexagonal wrench to operate the valve stems.

7). Mount the valve stems nuts and the service port cap

Be sure to use a torque wrench to tighten the service port cap to a torque 18N.m.

Be sure to check the gas leakage.

## 7.7 Re-installation while the outdoor unit need to be repaired

1. Evacuation for the whole system

Procedure:

1). Confirm that both the 2-way and 3-way valves are set to the opened position.

2). Connect the vacuum pump to 3-way valve’s service port.

3). Evacuation for approximately one hour. Confirm that the compound meter indicates -0.1Mpa.

4). Close the valve (Low side) on the charge set, turn off the vacuum pump, and confirm that the gauge needle does not move (approximately 5 minutes after turning off the vacuum pump).

5). Disconnect the charge hose from the vacuum pump.

2. Refrigerant charging

Procedure:

1). Connect the charge hose to the charging cylinder, open the 2-way valve and the 3-way valve

Connect the charge hose which you disconnected from the vacuum pump to the valve at the bottom of the cylinder. If the refrigerant is R410A, make the cylinder bottom up to ensure liquid charge.

2). Purge the air from the charge hose

Open the valve at the bottom of the cylinder and press the check valve on the charge set to purge the air (be careful of the liquid refrigerant).

3) Put the charging cylinder onto the electronic scale and record the weight.

4). Open the valves (Low side) on the charge set and charge the system with liquid refrigerant

If the system cannot be charge with the specified amount of refrigerant, or can be charged with a little at a time (approximately 150g each time) , operating the air conditioner in the cooling cycle; however, one time is not sufficient, wait approximately 1 minute and then repeat the procedure.

5).When the electronic scale displays the proper weight, disconnect the charge hose from the 3-way valve’s service port immediately

If the system has been charged with liquid refrigerant while operating the air conditioner, turn off the air conditioner before disconnecting the hose.

6). Mounted the valve stem caps and the service port

Use torque wrench to tighten the service port cap to a torque of 18N.m.

Be sure to check for gas leakage

# Electronic control function

8.1 Abbreviation

T1:  Indoor ambient temperature

T2:  Coil temperature of indoor heat exchanger middle.

T2B: Coil temperature of indoor heat exchanger outlet.

T3:  Coil temperature of outdoor heat exchanger

T4:  Outdoor ambient temperature

T5:  Compressor discharge temperature

Ts:  Setting temperature

8.2 Electric control working environment.

8.2.1 Input voltage: 198V --- 264V.

8.2.2 Input power frequency:50Hz.

8.2.3 Indoor fan normal working amp. is less than 1A.

8.2.4 Outdoor fan. Normal working amp. is less than 1.5A.

8.2.5 Four-way valve normal working amp. is less than 1A.

8.3 Outdoor unit’s digital display tube

There is a digital display tube in outdoor PCB.

Digital display tube display function

- In standby , the LED displays “- -”

- In compressor operation, the LED display the running frequency,

- In defrosting mode, The LED displays “dF” or alternative displays between running frequency and

“dF”(each displays 0.5s)

- In compressor pre-heating, The LED displays “PH” or alternative displays between running frequency

and “PH”(each displays 0.5s)

- During the oil return process, The LED displays “RO” or alternative displays between running

frequency  and “RO”(each displays 0.5s)

- In low ambient cooling mode, the LED displays “LC” or alternative displays between running

frequency  and “LC”(each displays 0.5s)

- In forced cooling mode, the LED displays “FC” or alternative displays between running frequency  and

“FC”(each displays 0.5s)

- When PFC module protection occurs three times within 15 minutes, the LED displays “E6” or

alternative displays between running frequency  and “E6”(each displays 0.5s)

- In protection or malfunction, the LED displays error code or protection code.

8.4 Outdoor unit point check function

There is a check switch in outdoor PCB.

Press the switch N times it will display the content corresponding to No. N. After getting into the check function, it will display No. N with 1.5s, meanwhile the low bit decimal of digit display flashing, indicated to get into the check function display. After 1.5s, it will display the content corresponding to No. N.

the digital display tube will display the follow procedure when push SW1 each time.

|  | Display | Remark |
| --- | --- | --- |
| 0 | Normal display | Display running frequency, running state or malfunction code |
| 1 | No. of indoor units in good connection | Actual data |
| 2 | Outdoor unit running mode code | Off:0,Fan only 1, Cooling:2, Heating:3, Forced cooling:4 |
| 3 | A indoor unit capacity | The capacity unit is horse power. If the indoor unit is not connected, the digital display tube will show: “――” (7K:0.8HP, 9K:1HP,12K:1.2HP,18K:1.5HP) |
| 4 | B indoor unit capacity |  |
| 5 | C indoor unit capacity |  |
| 6 | D indoor unit capacity |  |
| 7 | E indoor unit capacity |  |
| 8 | A Indoor unit capacity demand code | Norm value*HP (7K:0.8HP, 9K:1HP,12K:1.2HP,18K:1.5HP) |
| 9 | B Indoor unit capacity demand code |  |
| 10 | C Indoor unit capacity demand code |  |
| 11 | D Indoor unit capacity demand code |  |
| 12 | E Indoor unit capacity demand code |  |
| 13 | Total indoor units amendatory capacity demand code | Forced cooling:7 |
| 14 | The frequency corresponding to the total indoor units amendatory capacity demand |  |
| 15 | The frequency after the frequency limit |  |
| 16 | The frequency sending to compressor control chip |  |
| 17 | A indoor unit evaporator outlet temp.(T2BA) | If the temp. is lower than -9 degree, the digital display tube will show “-9”.If the temp. is higher than 70 degree, the digital display tube will show “70”. If the indoor unit is not connected, the digital display tube will show: “――” |
| 18 | B indoor unit evaporator outlet temp.(T2BB) |  |
| 19 | C indoor unit evaporator outlet temp.(T2BC) |  |
| 20 | D indoor unit evaporator outlet temp.(T2BD) |  |
| 21 | E indoor unit evaporator outlet temp.(T2BE) |  |
| 22 | A indoor unit room temp.(T1A) | If the temp. is lower than 0 degree, the digital display tube will show “0”.If the temp. is higher than 50 degree, the digital display tube will show “50”. If the indoor unit is not connected, the digital display tube will show: “――” |
| 23 | B indoor unit room temp.(T1B) |  |
| 24 | C indoor unit room temp.(T1C) |  |
| 25 | D indoor unit room temp.(T1D) |  |
| 26 | E indoor unit room temp.(T1E) |  |
| 27 | A indoor unit evaporator temp.(T2A) | If the temp. is lower than -9 degree, the digital display tube will show “-9”.If the temp. is higher than 70 degree, the digital display tube will show “70”. If the indoor unit is not connected, the digital display tube will show: “――” |
| 28 | B indoor unit evaporator temp.(T2B) |  |
| 29 | C indoor unit evaporator temp.(T2C) |  |
| 30 | D indoor unit evaporator temp.(T2D) |  |
| 31 | E indoor unit evaporator temp.(T2E) |  |
| 32 | Condenser pipe temp.(T3) |  |
| 33 | Outdoor ambient temp.(T4) |  |
| 34 | Compressor discharge temp.(Tp) | The display value is between 30~129 degree. If the temp. is lower than 30 degree, the digital display tube will show “30”.If the temp. is higher than 99 degree, the digital display tube will show single digit and tens digit. For example, the digital display tube show “0.5”,it means the compressor discharge temp. is 105 degree.) |
| 35 | AD value of current | The display value is hex number. For example ,the digital display tube show “Cd”, it means AD value is 205. |
| 36 | AD value of voltage |  |
| 37 | EXV open angle for A indoor unit | Actual data/4. If the value is higher than 99, the digital display tube will show single digit and tens digit. For example ,the digital display tube show “2.0”,it means the EXV open angle is 120×4=480p.) |
| 38 | EXV open angle for B indoor unit |  |
| 39 | EXV open angle for C indoor unit |  |
| 40 | EXV open angle for D indoor unit |  |
| 41 | EXV open angle for E indoor unit |  |
| 42 | Frequency limit symbol | Bit7 | Frequency limit caused by IGBT radiator | The display value is hex number. For example, the digital display tube show 2A,then Bit5=1, Bit3=1, Bit1=1. It means frequency limit caused by T4,T3 and current. |
|  |  | Bit6 | Frequency limit caused by PFC |  |
|  |  | Bit5 | Frequency limit caused by T4. |  |
|  |  | Bit4 | Frequency limit caused by T2. |  |
|  |  | Bit3 | Frequency limit caused by T3. |  |
|  |  | Bit2 | Frequency limit caused by Tp. |  |
|  |  | Bit1 | Frequency limit caused by current |  |
|  |  | Bit0 | Frequency limit caused by voltage |  |
| 43 | Average value of T2 | (Sum T2 value of all indoor units)/( number of indoor units in good connection) |
| 44 | Outdoor unit fan motor state | Off:0, High speed:1, Med speed:2, Low speed:3 Breeze:4, Super breeze:5 |
| 45 | The last error or protection code | 00 means no malfunction and protection |

The following items from 8.4.1 to 8.4.5 are for the explanation of the point check functions.

8.4.1 Frequency of compressor:

| Display | Frequency of compressor (Hz) |
| --- | --- |
| 30 | 30 |
| -- | Stand by |
| 60 | 60 |

8.4.2 Running mode:

| Display | Corresponding mode |
| --- | --- |
| 0 | Off |
| 1 | Fan only |
| 2 | Cooling mode |
| 3 | Heating mode |
| 4 | Forced cooling |

8.4.3 Capacity demand:

Cooling mode

| Capacity area | a | b | c | d | e | f |
| --- | --- | --- | --- | --- | --- | --- |
| Norm value (N) | 3 | 2 | 1.5 | 1 | 0.5 | 0 |

Heating mode

| Capacity area | a | b | c | d | e | f |
| --- | --- | --- | --- | --- | --- | --- |
| Norm value (N) | 3 | 2 | 1.5 | 1 | 0.5 | 0 |

8.4.4 Number of indoor unit

| Display | Number of indoor unit |
| --- | --- |
| 1 | 1 |
| 2 | 2 |
| 3 | 3 |
| 4 | 4 |
| 5 | 5 |

8.4.5 Opening degree of electronic expansion valve:

Actual opening degree equals the display data times 4

8.5 Protection

8.5.1 Three minutes delay at restart for compressor.

8.5.2 Temperature protection of compressor discharge.

When the compressor discharge temp. is getting higher, the running frequency will be limited as below rules:

----If 102℃<T5<115℃, decrease the frequency to the lower level every 2 minutes till to F1.

---If T5>115℃ for 10 seconds, the compressor will stop and restart till T5<90℃.

8.5.4 Compressor current limit protection

If the compressor current exceeds the current limit value for 10 seconds, the compressor frequency will be limited as below table.

Cooling mode:

| Current frequency（Hz） | Current limit value（A） | Frequency limit |
| --- | --- | --- |
| COOL_F16 | ICOOLLMT12 | Decrease the frequency to COOL_F4 and run at COOL_F4 for 3 minutes. After that, the frequency will be adjusted according to the capacity demand and rise to the upper level every 3 minutes (When the frequency>COOL_F4 via capacity demand). |
| COOL_F15 | ICOOLLMT11 |  |
| COOL_F14 | ICOOLLMT10 |  |
| COOL_F13 | ICOOLLMT9 |  |
| COOL_F12 | ICOOLLMT8 |  |
| COOL_F11 | ICOOLLMT7 |  |
| COOL_F10 | ICOOLLMT6 |  |
| COOL_F9 | ICOOLLMT5 |  |
| COOL_F8 | ICOOLLMT4 |  |
| COOL_F7 | ICOOLLMT3 |  |
| COOL_F6 | ICOOLLMT2 |  |
| COOL_F5 | ICOOLLMT1 |  |
| If the current frequency is lower than COOL_F4, the frequency will not be limited. After 10s of the compressor start, if the current>ICOOL, the AC will display the failure for 30 seconds and stop. The AC will restart 3 minutes later. |

Heating mode:

| Current frequency（Hz） | Current limit value（A） | Frequency limit |
| --- | --- | --- |
| HEAT_F16 | IHEATLMT12 | Decrease the frequency to HEAT_F4 and run at HEAT_F4 for 3 minutes. After that, the frequency will be adjusted according to the capacity demand and rise to the upper level every 3 minutes (When the frequency>Heat_F4 via capacity demand). |
| HEAT_F15 | IHEATLMT11 |  |
| HEAT_F14 | IHEATLMT10 |  |
| HEAT_F13 | IHEATLMT9 |  |
| HEAT_F12 | IHEATLMT8 |  |
| HEAT_F11 | IHEATLMT7 |  |
| HEAT_F10 | IHEATLMT6 |  |
| HEAT_F9 | IHEATLMT5 |  |
| HEAT_F8 | IHEATLMT4 |  |
| HEAT_F7 | IHEATLMT3 |  |
| HEAT_F6 | IHEATLMT2 |  |
| HEAT_F5 | IHEATLMT1 |  |
| If the current frequency is lower than HEAT_F4, the frequency will not be limited. After 10s of the compressor start, if the current>IHEAT, the AC will display the failure for 30 seconds and stop. The AC will restart 3 minutes later. |

8.5.5 Indoor / outdoor units communication protection

If the indoor units can not receive the feedback signal from the outdoor units for 2 minutes, the AC will stop and display the failure.

8.5.6 High condenser coil temp. protection.

When T3>65℃ for 3 seconds, the compressor will stop while the indoor fan and outdoor fan will continue.

When T3<52℃, the protection will release and the compressor will restart after 3 minutes.

8.5.7 Outdoor unit anti-freezing protection

When T2B<0℃ for 250 seconds, the indoor unit capacity demand will be zero and resume to normal when T2B>10℃.

8.5.8 Oil return

Running rules:

1. If the compressor frequency keeps lower than RET_OIL_FREQ1_ADD for RET_OIL_TIME1_ADD, the AC will rise the frequency  to RET_OIL_FREQ2_ADD for RET_OIL_TIME2_ADD and then resume to former frequency.

2. The EXV will keep 300p while the indoor units will keep the current running mode.

If the outdoor ambient is higher than TempT4HeatLimit_ADD during the oil return, the AC quit oil return.

# Troubleshooting

  - Indoor unit error code explanation:

PREMIER series +OASIS series+9A series +R series +12F series:

| Display | Operation lamp flash times | Timer lamp | Failure |
| --- | --- | --- | --- |
| E0 | 1 | X | Indoor EEPROM malfunction |
| E1 | 2 | X | Indoor / outdoor units communication error |
| E3 | 4 | X | Indoor fan speed has been out of control |
| E4 | 5 | X | Open or short circuit of T1 temperature sensor |
| E5 | 6 | X | Open or short circuit of T2 temperature sensor |
| F1 | 2 | O | Open or short circuit of T4 temperature sensor |
| F2 | 3 | O | Open or short circuit of T3 temperature sensor |
| F3 | 4 | O | Open or short circuit of T5 temperature sensor |
| F4 | 5 | O | Outdoor EEPROM parameter error |
| F5 | 6 | O | Outdoor fan speed out of control |
| F6 | 7 | O | Open or short circuit of T2B temperature sensor |
| P0 | 1 | ☆ | IPM module protection |
| P1 | 2 | ☆ | Voltage protection |
| P4 | 5 | ☆ | Inverter compressor drive protection |
| P5 | 6 | ☆ | Mode conflict |
| P6 | 7 | ☆ | Low pressure protection(Just matching with M4OA-36HFN1-Q) |

O   （light）  X   （off）     ☆ （flash）

Light Commercial series(Except Console)

| NO. | MALFUNCTION | RUN | Timer | DEF | Alarm | DISPLAY DIGITAL TUBE |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Open or short circuit of T1 temperature sensor | ☆ | X | X | X | E0 |
| 2 | Open or short circuit of T2 temperature sensor | X | X | ☆ | X | E1 |
| 3 | Indoor / outdoor units communication error | X | ☆ | X | X | E2 |
| 4 | Full-water malfunction | X | X | X | ☆ | E3 |
| 5 | Indoor EEPROM malfunction | ☆ | ☆ | X | X | E4 |
| 6 | IPM module protection | ☆ | X | X | O | E5 |
| 7 | Open or short circuit of T3 or T4 temperature sensor or Outdoor EEPROM malfunction | ☆ | O | X | X | E6 |
| 8 | Outdoor fan speed has been out of control | ☆ | O | ☆ | X | E7 |
| 9 | Indoor fan speed has been out of control | ☆ | O | O | X | F5 |
| 10 | Voltage protection | ☆ | O | X | O | P0 |
| 12 | Outdoor unit over-current protection | ☆ | ☆ | ☆ | X | P2 |
| 13 | Inverter compressor drive protection | ☆ | ◎ | X | X | P4 |
| 14 | Mode conflict | ☆ | X | O | O | P5 |
| Flash(at 2.5Hz) ◎ Flash(at 0.5Hz) O light X（off） Note: Digital display is only available for A5 duct type. |

For Console

| NO. | Malfunction | Running lamp | Timer lamp | Defrosting lamp |
| --- | --- | --- | --- | --- |
| 1 | Open or short circuit of T1 temperature sensor | ☆ | X | X |
| 2 | Open or short circuit of T2 temperature sensor | X | X | ☆ |
| 3 | Communication malfunction between indoor and outdoor units. | X | ☆ | X |
| 4 | Outdoor fan speed has been out of control | X | ☆ | O |
| 5 | Indoor EEPROM malfunction | ☆ | ☆ | X |
| 6 | IPM module protection | ☆ | X | ☆ |
| 7 | Open or short circuit of T3 or T4 temperature sensor or Outdoor unit EEPROM parameter error | ☆ | ☆ | ☆ |
| 8 | Voltage protection | ☆ | ☆ | O |
| 10 | Inverter compressor drive protection | ☆ | ◎ | X |
| 11 | Indoor fan Speed has been out of control. | ☆ | O | ☆ |
| 12 | Mode conflict | ☆ | X | O |
| O(light) X(off) ☆(flash at 5Hz) ◎(flash at 0.5Hz) |

  - Outdoor unit error code explanation:

| Display | LED STATUS |
| --- | --- |
| E0 | Outdoor EEPROM malfunction |
| E2 | Indoor / outdoor units communication error |
| E3 | Communication malfunction between IPM board and outdoor main board |
| E4 | Open or short circuit of outdoor unit temperature sensor |
| E5 | Voltage protection |
| E6 | PFC module protection (For M4OA-36HFN1-Q, M4OD-28HFN1-Q, M5OC-36HFN1-Q) |
| E8 | Outdoor fan speed has been out of control |
| F1 | No A Indoor unit coil outlet temperature sensor or connector of sensor is defective |
| F2 | No B Indoor unit coil outlet temperature sensor or connector of sensor is defective |
| F3 | No C Indoor unit coil outlet temperature sensor or connector of sensor is defective |
| F4 | No D Indoor unit coil outlet temperature sensor or connector of sensor is defective |
| F5 | No E Indoor unit coil outlet temperature sensor or connector of sensor is defective |
| P1 | High pressure protection (For M4OA-36HFN1-Q, M4OD-28HFN1-Q, M5OC-36HFN1-Q) |
| P2 | Low pressure protection (For M4OA-36HFN1-Q, M4OD-28HFN1-Q, M5OC-36HFN1-Q) |
| P3 | Current protection of compressor |
| P4 | Temperature protection of compressor discharge |
| P5 | High temperature protection of condenser |
| P6 | IPM module protection |

Note: Once these error codes display, they will disappear in at least 30 seconds if the unit come back to normal.(Except E3&E4)

9.3 Trouble shooting

9.3.1 For the indoor unit

9.3.1.1 Indoor EEPROM malfunction

9.3.1.2 Indoor / outdoor units communication error

9.3.1.3 indoor unit fan speed has been out of control

Index 1:

1.Indoor AC fan motor

Measure the resistance value of each winding by using the tester.

For the definite value of the resistance, refer to 9.4 Main parts check.

2.Indoor DC fan motor(control chip is inside fan motor)

Measure the resistance value of each winding by using the tester. If any resistance value is zero, the fan motor must have problems and need to be replaced.

For other models:

| NO. | Color |
| --- | --- |
| 1 | Red |
| 2 | --- |
| 3 | Black |
| 4 | White |
| 5 | Yellow |
| 6 | Blue |

For console:

| NO. | Color |
| --- | --- |
| 1 | Red |
| 2 | --- |
| 3 | White |
| 4 | Blue |
| 5 | Yellow |
| 6 | Black |

Index2:

1: Indoor AC fan motor

Power on and set the unit running in fan mode at high fan speed. After running for 15 seconds, measure the voltage of pin1 and pin2. If the value of the voltage is less than 100V(208~240V power supply)or 50V(115V power supply), the PCB must have problems and need to be replaced.

2. Indoor DC fan motor(control chip is inside fan motor)

Power on and when the unit is in standby, measure the voltage of pin1-pin3, pin4-pin3 in fan motor connector. If the value of the voltage is not in the range showing in below table, the PCB must have problems and need to be replaced.

For other models:

For console:

DC motor voltage input and output

For split type:

| NO. | Color | Signal | Voltage |
| --- | --- | --- | --- |
| 1 | Red | Vs/Vm | 280V~380V |
| 2 | --- | --- | --- |
| 3 | Black | GND | 0V |
| 4 | White | Vcc | 14-17.5V |
| 5 | Yellow | Vsp | 0~5.6V |
| 6 | Blue | FG | 14-17.5V |

For A5 Duct & Four-way cassette (compact)

| NO. | Color | Signal | Voltage |
| --- | --- | --- | --- |
| 1 | Red | Vs/Vm | 192V~380V |
| 2 | --- | --- | --- |
| 3 | Black | GND | 0V |
| 4 | White | Vcc | 13.5-16.5V |
| 5 | Yellow | Vsp | 0~6.5V |
| 6 | Blue | FG | 15V |

For console:

| NO. | Color | Signal | Voltage |
| --- | --- | --- | --- |
| 1 | Red | VDC | 310V |
| 2 | --- | --- | --- |
| 3 | White | Vcc | 15V |
| 4 | Blue | FG | 15V |
| 5 | Yellow | Vsp | 0-7.5V |
| 6 | Black | GND | 0V |

9.3.1.4 Open or short circuit of temperature sensor.

9.3.1.6 Full-water malfunction

9.3.2 For the outdoor unit

9.3.2 1 Outdoor EEPROM malfunction(ODU E0)

9.3.2.2 Communication malfunction between IPM board and outdoor main board(ODU E3)

9.3.2.3 Voltage protection(ODU E5)

9.3.2.4 PFC module protection (ODU E6) (For U2MRSL(4)-36, U2MRSL(4)-28, U2MRSL(5)-36)

9.3.2.5 Outdoor unit fan speed has been out of control (E8)

Index 1:

1.Outdoor DC fan motor(control chip is inside fan motor)

Measure the resistance value of each winding by using the tester. If any resistance value is zero, the fan motor must have problems and need to be replaced.

| NO. | Color |
| --- | --- |
| 1 | Red |
| 2 | --- |
| 3 | Black |
| 4 | White |
| 5 | Yellow |
| 6 | Blue |

Index2:

1. Outdoor DC fan motor(control chip is inside fan motor)

Power on and when the unit is in standby, measure the voltage of pin1-pin3, pin4-pin3 in fan motor connector. If the value of the voltage is not in the range showing in below table, the PCB must have problems and need to be replaced.

For other models:

DC motor voltage input and output

| NO. | Color | Signal | Voltage |
| --- | --- | --- | --- |
| 1 | Red | Vs/Vm | 140V~380V |
| 2 | --- | --- | --- |
| 3 | Black | GND | 0V |
| 4 | White | Vcc | 13.5-16.5V |
| 5 | Yellow | Vsp | 0~6.5V |
| 6 | Blue | FG | 15V |

9.3.2.6 High pressure protection (ODU P1) (For U2MRSL(4)-36, U2MRSL(4)-28, U2MRSL(5)-36)

9.3.2.7 Low pressure protection (ODU P2) (For U2MRSL(4)-36, U2MRSL(4)-28, U2MRSL(5)-36)

9.3.2.8 Current protection of compressor(ODU P3)

9.3.2.4 Temperature protection of compressor discharge(ODU P4)

9.3.2.9 High temperature protection of condenser(ODU P5)

When outdoor pipe temperature is more than  65°C, the unit will stop, and unit runs again when outdoor pipe temp. less than  52°C.

9.3.2.10 IPM module protection(ODU P6)

  - Main parts check

Spec.

| Indoor unit |
| --- |
| Model | 7K 11M | 9K 11M | 12K 11M | 18K 11M |
| Indoor fan motor | WZDK20-38G | WZDK20-38G | WZDK20-38G | WZDK58-38G |
| Model |  | 9K 11P | 12K 11P | 18K 11P |
| Indoor fan motor |  | WZDK20-38G | WZDK20-38G | WZDK20-38G |
| Model | 7K 9A | 9K 9A | 12K 9A | 18K(RC8) 9A | 18K(RC4) 9A |
| Indoor fan motor | WZDK20-38G | RPG20D | RPG20D | WZDK30-38G | RPG28D |
| Model | 7K 12F | 9K 12F | 12K 12F | 18K 12F |
| Indoor fan motor | RPG20E | RPG20E | WZDK20-38G | WZDK30-38G |
| Model | 7K R | 9K R | 12K R | 18K R |
| Indoor fan motor | RPG13H | RPG13H | RPG20E | RPG25 |
| Model | 7K A5 | 9K A5 | 12K A5 | 18K A5 |
| Indoor fan motor | WZDK27-38GS | WZDK27-38GS | WZDK27-38GS | YSK68-4P |
| Model | 7K Cassette | 9K Cassette | 12K Cassette | 18K Cassette |
| Indoor fan motor | WZDK37-38G | WZDK37-38G | WZDK37-38G | YDK37-4P |
| Model |  | 9K Console | 12K Console | 18K Console |
| Indoor fan motor |  | RD-280-20-8A | RD-280-20-8A | RD-280-20-8A |
| Outdoor unit |
| Model | 1x2(14k) | 1x2(18k) | 1x3(27K) | 1x3(21K) |
| Compressor | DA130M1C-31FZ | DA150S1C-20FZ | DA250S2C-30MT | DA150S1C-20FZ |
| Outdoor fan motor | WZDK50-38G | WZDK50-38G | WZDK72-38G | WZDK50-38G |
| Model | 1x4(28K) | 1x4(36K) | 1x5 |  |
| Compressor | DA250S2C-30MT | TNB306FPGMC-L | TNB306FPGMC-L |  |
| Outdoor fan motor | WZDK72-38G | WZDK180-38G | WZDK180-38G |  |

  - Temperature sensor checking

Disconnect the temperature sensor from PCB, measure the resistance value with a tester.

Temperature Sensors.

Room temp.(T1) sensor,

Indoor coil temp.(T2) sensor,

Outdoor coil temp.(T3) sensor,

Outdoor ambient temp.(T4) sensor,

Compressor discharge temp.(T5) sensor.

Measure the resistance value of each winding by using the multi-meter.

Appendix 1 Temperature Sensor Resistance Value Table for T1,T2,T3,T4 (℃--K)

| ℃ | K Ohm | ℃ | K Ohm | ℃ | K Ohm | ℃ | K Ohm |
| --- | --- | --- | --- | --- | --- | --- | --- |
| -20 | 115.266 | 20 | 12.6431 | 60 | 2.35774 | 100 | 0.62973 |
| -19 | 108.146 | 21 | 12.0561 | 61 | 2.27249 | 101 | 0.61148 |
| -18 | 101.517 | 22 | 11.5000 | 62 | 2.19073 | 102 | 0.59386 |
| -17 | 96.3423 | 23 | 10.9731 | 63 | 2.11241 | 103 | 0.57683 |
| -16 | 89.5865 | 24 | 10.4736 | 64 | 2.03732 | 104 | 0.56038 |
| -15 | 84.2190 | 25 | 10.000 | 65 | 1.96532 | 105 | 0.54448 |
| -14 | 79.3110 | 26 | 9.55074 | 66 | 1.89627 | 106 | 0.52912 |
| -13 | 74.5360 | 27 | 9.12445 | 67 | 1.83003 | 107 | 0.51426 |
| -12 | 70.1698 | 28 | 8.71983 | 68 | 1.76647 | 108 | 0.49989 |
| -11 | 66.0898 | 29 | 8.33566 | 69 | 1.70547 | 109 | 0.48600 |
| -10 | 62.2756 | 30 | 7.97078 | 70 | 1.64691 | 110 | 0.47256 |
| -9 | 58.7079 | 31 | 7.62411 | 71 | 1.59068 | 111 | 0.45957 |
| -8 | 56.3694 | 32 | 7.29464 | 72 | 1.53668 | 112 | 0.44699 |
| -7 | 52.2438 | 33 | 6.98142 | 73 | 1.48481 | 113 | 0.43482 |
| -6 | 49.3161 | 34 | 6.68355 | 74 | 1.43498 | 114 | 0.42304 |
| -5 | 46.5725 | 35 | 6.40021 | 75 | 1.38703 | 115 | 0.41164 |
| -4 | 44.0000 | 36 | 6.13059 | 76 | 1.34105 | 116 | 0.40060 |
| -3 | 41.5878 | 37 | 5.87359 | 77 | 1.29078 | 117 | 0.38991 |
| -2 | 39.8239 | 38 | 5.62961 | 78 | 1.25423 | 118 | 0.37956 |
| -1 | 37.1988 | 39 | 5.39689 | 79 | 1.21330 | 119 | 0.36954 |
| 0 | 35.2024 | 40 | 5.17519 | 80 | 1.17393 | 120 | 0.35982 |
| 1 | 33.3269 | 41 | 4.96392 | 81 | 1.13604 | 121 | 0.35042 |
| 2 | 31.5635 | 42 | 4.76253 | 82 | 1.09958 | 122 | 0.3413 |
| 3 | 29.9058 | 43 | 4.57050 | 83 | 1.06448 | 123 | 0.33246 |
| 4 | 28.3459 | 44 | 4.38736 | 84 | 1.03069 | 124 | 0.32390 |
| 5 | 26.8778 | 45 | 4.21263 | 85 | 0.99815 | 125 | 0.31559 |
| 6 | 25.4954 | 46 | 4.04589 | 86 | 0.96681 | 126 | 0.30754 |
| 7 | 24.1932 | 47 | 3.88673 | 87 | 0.93662 | 127 | 0.29974 |
| 8 | 22.5662 | 48 | 3.73476 | 88 | 0.90753 | 128 | 0.29216 |
| 9 | 21.8094 | 49 | 3.58962 | 89 | 0.87950 | 129 | 0.28482 |
| 10 | 20.7184 | 50 | 3.45097 | 90 | 0.85248 | 130 | 0.27770 |
| 11 | 19.6891 | 51 | 3.31847 | 91 | 0.82643 | 131 | 0.27078 |
| 12 | 18.7177 | 52 | 3.19183 | 92 | 0.80132 | 132 | 0.26408 |
| 13 | 17.8005 | 53 | 3.07075 | 93 | 0.77709 | 133 | 0.25757 |
| 14 | 16.9341 | 54 | 2.95896 | 94 | 0.75373 | 134 | 0.25125 |
| 15 | 16.1156 | 55 | 2.84421 | 95 | 0.73119 | 135 | 0.24512 |
| 16 | 15.3418 | 56 | 2.73823 | 96 | 0.70944 | 136 | 0.23916 |
| 17 | 14.6181 | 57 | 2.63682 | 97 | 0.68844 | 137 | 0.23338 |
| 18 | 13.9180 | 58 | 2.53973 | 98 | 0.66818 | 138 | 0.22776 |
| 19 | 13.2631 | 59 | 2.44677 | 99 | 0.64862 | 139 | 0.22231 |

Appendix 2 Temperature Sensor Resistance Value Table for T5 (℃--K)

| ℃ | K Ohm | ℃ | K Ohm | ℃ | K Ohm | ℃ | K Ohm |
| --- | --- | --- | --- | --- | --- | --- | --- |
| -20 | 542.7 | 20 | 68.66 | 60 | 13.59 | 100 | 3.702 |
| -19 | 511.9 | 21 | 65.62 | 61 | 13.11 | 101 | 3.595 |
| -18 | 483 | 22 | 62.73 | 62 | 12.65 | 102 | 3.492 |
| -17 | 455.9 | 23 | 59.98 | 63 | 12.21 | 103 | 3.392 |
| -16 | 430.5 | 24 | 57.37 | 64 | 11.79 | 104 | 3.296 |
| -15 | 406.7 | 25 | 54.89 | 65 | 11.38 | 105 | 3.203 |
| -14 | 384.3 | 26 | 52.53 | 66 | 10.99 | 106 | 3.113 |
| -13 | 363.3 | 27 | 50.28 | 67 | 10.61 | 107 | 3.025 |
| -12 | 343.6 | 28 | 48.14 | 68 | 10.25 | 108 | 2.941 |
| -11 | 325.1 | 29 | 46.11 | 69 | 9.902 | 109 | 2.86 |
| -10 | 307.7 | 30 | 44.17 | 70 | 9.569 | 110 | 2.781 |
| -9 | 291.3 | 31 | 42.33 | 71 | 9.248 | 111 | 2.704 |
| -8 | 275.9 | 32 | 40.57 | 72 | 8.94 | 112 | 2.63 |
| -7 | 261.4 | 33 | 38.89 | 73 | 8.643 | 113 | 2.559 |
| -6 | 247.8 | 34 | 37.3 | 74 | 8.358 | 114 | 2.489 |
| -5 | 234.9 | 35 | 35.78 | 75 | 8.084 | 115 | 2.422 |
| -4 | 222.8 | 36 | 34.32 | 76 | 7.82 | 116 | 2.357 |
| -3 | 211.4 | 37 | 32.94 | 77 | 7.566 | 117 | 2.294 |
| -2 | 200.7 | 38 | 31.62 | 78 | 7.321 | 118 | 2.233 |
| -1 | 190.5 | 39 | 30.36 | 79 | 7.086 | 119 | 2.174 |
| 0 | 180.9 | 40 | 29.15 | 80 | 6.859 | 120 | 2.117 |
| 1 | 171.9 | 41 | 28 | 81 | 6.641 | 121 | 2.061 |
| 2 | 163.3 | 42 | 26.9 | 82 | 6.43 | 122 | 2.007 |
| 3 | 155.2 | 43 | 25.86 | 83 | 6.228 | 123 | 1.955 |
| 4 | 147.6 | 44 | 24.85 | 84 | 6.033 | 124 | 1.905 |
| 5 | 140.4 | 45 | 23.89 | 85 | 5.844 | 125 | 1.856 |
| 6 | 133.5 | 46 | 22.89 | 86 | 5.663 | 126 | 1.808 |
| 7 | 127.1 | 47 | 22.1 | 87 | 5.488 | 127 | 1.762 |
| 8 | 121 | 48 | 21.26 | 88 | 5.32 | 128 | 1.717 |
| 9 | 115.2 | 49 | 20.46 | 89 | 5.157 | 129 | 1.674 |
| 10 | 109.8 | 50 | 19.69 | 90 | 5 | 130 | 1.632 |
| 11 | 104.6 | 51 | 18.96 | 91 | 4.849 |  |  |
| 12 | 99.69 | 52 | 18.26 | 92 | 4.703 |  |  |
| 13 | 95.05 | 53 | 17.58 | 93 | 4.562 |  |  |
| 14 | 90.66 | 54 | 16.94 | 94 | 4.426 |  |  |
| 15 | 86.49 | 55 | 16.32 | 95 | 4.294 | B(25/50)=3950K |
| 16 | 82.54 | 56 | 15.73 | 96 | 4.167 |  |  |
| 17 | 78.79 | 57 | 15.16 | 97 | 4.045 | R(90℃)=5KΩ±3% |
| 18 | 75.24 | 58 | 14.62 | 98 | 3.927 |  |  |
| 19 | 71.86 | 59 | 14.09 | 99 | 3.812 |  |  |

2.Compressor checking

Measure the resistance value of each winding by using the tester.

| Position |  | Resistance Value |
| --- | --- | --- |
|  | DA130M1C-31FZ | DA150S1C-20FZ | DA250S2C-30MT | TNB306FPGMC-L |
| Blue - Red | 1.77Ω(20℃) | 0.95Ω(20℃) | 0.55Ω(20℃) | 0.53Ω(20℃) |

3. IPM continuity check

Turn off the power, let the large capacity electrolytic capacitors discharge completely, and dismount the IPM. Use a digital tester to measure the resistance between P and UVWN; UVW and N.

| Digital tester | Normal resistance value | Digital tester | Normal resistance value |
| --- | --- | --- | --- |
| (+)Red | (-)Black | ∞ (Several MΩ) | (+)Red | (-)Black | ∞ (Several MΩ) |
| P | N |  | U | N |  |
|  | U |  | V |  |  |
|  | V |  | W |  |  |
|  | W |  | (+)Red |  |  |

4: Indoor AC Fan Motor

Measure the resistance value of each winding by using the tester.

| Position | Resistance Value |
| --- | --- |
|  | RPG20D(Weilng) | RPG28D(TongDe) | RPG28D(Dayang) | RPG20E(TongDe) | RPG20E(Weilng) | RPG13H(Weilng) | RPG25(TongDe) | YSK68-4P(Weilng) | YDK37-4P |
| Black - Red | 398Ω±8% (20℃) | 255Ω±8% (20℃) | 271.3Ω±8% (20℃) | 415Ω±8% (20℃) | 387Ω±8% (20℃) | 575Ω±8% (20℃) | 295Ω±8% (20℃) | 285.8Ω±8% (20℃) | 258.7Ω±8% (20℃) |
| Red - Yellow | 345Ω±8% (20℃) | 335Ω±8% (20℃) | 347.8Ω±8% (20℃) | 396Ω±8% (20℃) | 378Ω±8% (20℃) | 558Ω±8% (20℃) | 420Ω±8% (20℃) | 178.5Ω±8% (20℃) | 189.7Ω±8% (20℃) |
| Yellow - Blue | 345Ω±8% (20℃) | 335Ω±8% (20℃) | 347.8Ω±8% (20℃) | 396Ω±8% (20℃) | 378Ω±8% (20℃) | 558Ω±8% (20℃) | 420Ω±8% (20℃) | 178.5Ω±8% (20℃) | 189.7Ω±8% (20℃) |

# Text boxes

It is only operated in the heating operation mode except defrosting operation.

Outdoor unit

Power relay control

Hydrophilic aluminum fin

Anti-rust cabinet

Valve protection cover

Low noise air flow system

Discharge pipe temperature protection

4 way valve control

It protects the valves and prevents water from dripping.

The hydrophilic fin can improve the heating efficiency at operation mode.

(Indoor unit)

(Liquid side)

(Gas side)

Vacuum

pump

Vacuum

pump

Lo

Hi

Handle Hi

Two-way valve

Close

Manifold valve

Compound meter

Pressure

gauge

-0.1MPa

Handle Lo

Charge hose

Charge hose

(Outdoor unit)

Close

Three-way valve

Electronic scale

Electronic scale

Pic 1: check the voltage of N to S (Vs), is it moving alternately between positive value and negative value?

Pic 2: :IPM (For dual/tri-zone)

Self-Check

Operating

els)

Pic 2: :IPM (For qua-zone)

Self-Check

Power,

Operating

els)

PIC3 :Main board LED when power on and unit standby.

PIC 4: check point button,

Press 1 time for check how many indoor units are connected

.